## Slide 1
Update on Microchannel Cooling
J. Daguin (CERN PH/DT)
A. Mapelli (CERN PH/DT)
M. Morel (CERN PH/ESE)
J. Noel (CERN PH/DT)
G. Nuessle (UCL)
P. Petagna (CERN PH/DT)
New process / design optimized for SFB
First test results from SFB wafer
Integration issues

## Slide 2
Problems Solved with Silicon Fusion Bonding
Problem #1: surface roughness and polymer contamination after DRIE process
Problem #2: bonding surface between channels too small
Enhanced cleaning procedure
AFM Image of the surface BEFORE enhanced cleaning
(mean roughness ~ 10 nm)
AFM Image of the surface AFTER enhanced cleaning
(mean roughness < 0.7 nm)
Modified design, wall thickness = 100 mm (used to be 25 mm for Anodic Bonding)

## Slide 3
First Successful DRIE + SFB Cooling Wafer
IR image of a DRIE + SFB wafer with standard cleaning process
IR image of a DRIE + SFB wafer with enhanced cleaning process
IR image of a DRIE + SFB wafer with enhanced cleaning process + thermal annealing

## Slide 4
Expected X0 Impact for the SFB Design
Si
Thickness =150 μm
Channels:
100 x 100 μm or less
Readout chip
%X0 = 0,1 % ÷ 0,12 % (with 150 μm of Si and channels of 100x100 μm)
C6F14
C6F14

## Slide 5
Channels 100 µm deep
Manifolds 280 µm deep
Through holes
Frozen SFB Design for NA62 GTK
Wall thickness between channels: 100mm (optimized for SFB)

## Slide 6
Rectangular manifold, 1 mm wide, 100 mm thick, central inlet & outlet
Wedged manifold, 1.6 mm Max width, 150 mm thick
Wedged manifold, 1.6 mm Max width, 280 mm thick
Wedged manifold, 1.6 mm Max width, 400 mm thick
Calculated Effect of Manifold Geometry on Pressure
Initial design: simulation vs. measurement
Design optimization

## Slide 7
Measured Pressure Drops for New Design
Nominal flow rate for DT~5 °C with P=48 W

## Slide 8
Flow Distribution with New Design
Tfluid passes below the lower set sensitivity of the camera
IN
OUT
IN
OUT
Preliminary test to “visualize” the level of uniformity of the flow inside the cold plate: while circulating, the temperature of the fluid is progressively reduced below the lower threshold set for the thermal camera. As soon as the fluid reaches that temperature, the whole surface of the cold plate passes below the threshold in one go.

## Slide 9
“Visualization” of Flow Distribution: MOVIE
http://petagna.web.cern.ch/petagna/gtk%20movie/

## Slide 10
The New “GTKsym” Heater
Design: M. Morel
Production: R. De Oliveira

## Slide 11
GTK SFB Design under Test

## Slide 12
Very First SFB Design Heating Test
FLOW IN
FLOW OUT
HEATING SURFACE
Test under mild vacuum (2 ·10-2 mbar)
No detectable leak
P = 16 W (½ nominal)
Q = 0.0036 kg/s (½ nominal)
DTIN-OUT ~ 3.5 °C

## Slide 13
Integration in the NA62 GTK module
A test programme of the integration between cooling plate, sensor and readout chips has been started and will cover the following issues: choice of the bonding material, the handling of objects and the design of the mechanical supports.
M. Morel, A. Honma and I. McGill involved.

## Slide 14
Spin-coatable Adhesives Pre-selected
Staystik:
http://www.cooksonsemi.com/products/polymer/staystik.asp
http://www.microchem.com/products/su_eight.htm
SU8

## Slide 15
Basic Ideas about the Cooling Plant(s)
Standard design and components in use in several LHC experiments (EN/CV-DC)
Option A: 3 local small units (~15 kCHF each)
Option B: 1 larger unit with long transfer lines

## Slide 16
RESERVE SLIDES
?

## Slide 17
Chart: Manifold width (mm)
| 2 | 1 | 0.5 | 0.25 | 0.1
tp=50µ | 0.27 | 1.07 | 4.33 | 15.35 | 52.74
tp=200µ | 2.133 | 7.28 | 19.38 | 41.46
tp=350µ | 4.15 | 11.47 | 26.04 | 48.17
tp=525µ | 5.55 | 14.07 | 29.27 | 50.1
Pressure resistance vs. channel dimension
Chart: Rupture Pressure for Silicon Cover (165 Mpa)
| 0.1 | 0.25 | 0.5 | 1 | 2
tp=50µ | 397.4955 | 113.2644 | 32.3755 | 7.9101 | 1.876
tp=200µ | 336.0493 | 157.1567 | 58.6616 | 18.5388
tp=350µ | 390.5333 | 214.1152 | 92.3318 | 32.5532
tp=525µ | 396.4445 | 219.7361 | 95.2069 | 33.5737
RESERVE SLIDE

## Slide 18
RESERVE SLIDE
Radiation Length Values
Radiation length (X0): mean distance over which the energy of a high-energy electron is reduced to 1/e (0.37) by bremsstrahlung
(Dahl, PDG)
More readily usable quantity: X0 = X0/r [cm]
Cu: 1.436 cm
Steel: ~1.7 cm
Al alloy: ~8.9 cm
Ti: 3.56 cm
Si: 9.37 cm
K13D2U (70% vf): 23 cm
PEEK: 31.9 cm
C6F14 @ -20 C : 19.31 cm
C3F8(liquid) @ -20 C : 22.21 cm
CO2(liquid) @ -20 C: 35.84 cm